## Index
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
AMC REPORT CHECKLISTS – CONTROL COPY (Derived from SOP-01 to SOP-26)
Document |  | Checklist set CL-01 to CL-26 (IFSPL/M&M/CL/001–026)
Revision |  | 00
Effective Date |  | 01-10-2026 (aligned to SOP effective date)
Prepared by |  | Santosh Singh – Sr. Manager – Technical
Reviewed by |  | Prahlad Singh – VP – Technical
Approved by |  | Balagopal V – CEO
Signatures: Prepared ____________ Reviewed ____________ Approved ____________
CL No. | Checklist Doc. No. | Reference SOP Doc. No. | Equipment / Activity (SOP title) | No. of items | Go to sheet | Legacy workbook tab(s) covered
CL-01 | IFSPL/M&M/CL/001 | IFSPL/M&M/SOP/001 | Fire Hydrants & Fire Brigade Inlet Maintenance | 10 | Open › | Hyd-HB CL-01 (landing valve part); FEH
CL-02 | IFSPL/M&M/CL/002 | IFSPL/M&M/SOP/002 | Fixed & Portable Fire Water / Foam Monitors Maintenance | 10 | Open › | F-Monitor CL-02; W-Monitor
CL-03 | IFSPL/M&M/CL/003 | IFSPL/M&M/SOP/003 | Delivery Hose Boxes Maintenance | 8 | Open › | Hyd-HB CL-01 (hose box part)
CL-04 | IFSPL/M&M/CL/004 | IFSPL/M&M/SOP/004 | Foam Pourer / Foam Maker Systems Maintenance | 8 | Open › | — (no equivalent tab in legacy workbook)
CL-05 | IFSPL/M&M/CL/005 | IFSPL/M&M/SOP/005 | Water Spray & Drencher Systems Maintenance | 8 | Open › | Sprinkler-WC; Sprinkler System (hidden)
CL-06 | IFSPL/M&M/CL/006 | IFSPL/M&M/SOP/006 | Foam Trolley Maintenance | 7 | Open › | F Trolly
CL-07 | IFSPL/M&M/CL/007 | IFSPL/M&M/SOP/007 | Mobile Trolley Mounted DCP Systems Maintenance (150 Kg) | 9 | Open › | — (no equivalent tab in legacy workbook)
CL-08 | IFSPL/M&M/CL/008 | IFSPL/M&M/SOP/008 | Fire Water Deluge Valves Maintenance | 7 | Open › | — (no equivalent tab in legacy workbook)
CL-09 | IFSPL/M&M/CL/009 | IFSPL/M&M/SOP/009 | First Aid Fire Hose Reels Maintenance | 7 | Open › | Hose Reel
CL-10 | IFSPL/M&M/CL/010 | IFSPL/M&M/SOP/010 | Fire Vehicles – Associated Water / Foam Systems Maintenance | 7 | Open › | — (no equivalent tab in legacy workbook)
CL-11 | IFSPL/M&M/CL/011 | IFSPL/M&M/SOP/011 | Hydro Testing & Pressurisation of Fire Extinguishers | 9 | Open › | (Extinguisher tabs – hydro-test only, see mapping)
CL-12 | IFSPL/M&M/CL/012 | IFSPL/M&M/SOP/012 | Mechanical Medium Expansion Foam Generators Maintenance | 7 | Open › | — (no equivalent tab in legacy workbook)
CL-13 | IFSPL/M&M/CL/013 | IFSPL/M&M/SOP/013 | Clean Agent / CO2 Fire Suppression Systems Maintenance | 10 | Open › | — (no equivalent tab in legacy workbook)
CL-14 | IFSPL/M&M/CL/014 | IFSPL/M&M/SOP/014 | DCP Systems of Fire Tenders Maintenance | 9 | Open › | — (no equivalent tab in legacy workbook)
CL-15 | IFSPL/M&M/CL/015 | IFSPL/M&M/SOP/015 | Isolation Valves of Fire Water Network Maintenance | 7 | Open › | — (no equivalent tab in legacy workbook)
CL-16 | IFSPL/M&M/CL/016 | IFSPL/M&M/SOP/016 | Cleaning of Fire Water Tanks at Fire Stations | 6 | Open › | — (no equivalent tab in legacy workbook)
CL-17 | IFSPL/M&M/CL/017 | IFSPL/M&M/SOP/017 | Fire Buckets & Bucket Stands Maintenance | 5 | Open › | — (no equivalent tab in legacy workbook)
CL-18 | IFSPL/M&M/CL/018 | IFSPL/M&M/SOP/018 | Fire Detection & Alarm Systems Maintenance | 7 | Open › | — (no equivalent tab in legacy workbook)
CL-19 | IFSPL/M&M/CL/019 | IFSPL/M&M/SOP/019 | Inline Foam Inductors Maintenance | 4 | Open › | — (no equivalent tab in legacy workbook)
CL-20 | IFSPL/M&M/CL/020 | IFSPL/M&M/SOP/020 | Cleaning of Foam & Water Tanks of Fire Vehicles | 7 | Open › | — (no equivalent tab in legacy workbook)
CL-21 | IFSPL/M&M/CL/021 | IFSPL/M&M/SOP/021 | Cleaning of Overhead Foam Storage Tanks | 6 | Open › | — (no equivalent tab in legacy workbook)
CL-22 | IFSPL/M&M/CL/022 | IFSPL/M&M/SOP/022 | Servicing & Hydro Testing of CA Foam / Water Mist Extinguishers | 7 | Open › | — (no equivalent tab in legacy workbook)
CL-23 | IFSPL/M&M/CL/023 | IFSPL/M&M/SOP/023 | Servicing & Hydro Testing of Air Compressors (Tyre Air Filling) | 7 | Open › | — (no equivalent tab in legacy workbook)
CL-24 | IFSPL/M&M/CL/024 | IFSPL/M&M/SOP/024 | Calibration of Weighing Machines | 5 | Open › | — (no equivalent tab in legacy workbook)
CL-25 | IFSPL/M&M/CL/025 | IFSPL/M&M/SOP/025 | Servicing & Calibration of Digital Level Indicators (Overhead Foam Tank) | 4 | Open › | — (no equivalent tab in legacy workbook)
CL-26 | IFSPL/M&M/CL/026 | IFSPL/M&M/SOP/026 | Hanging & Mounting of Portable Fire Extinguishers | 4 | Open › | (Extinguisher tabs – mounting only, see mapping)
HOW TO USE THIS CONTROL COPY
1. One tab per SOP. Tab CL-nn is built from Section 6 (Check List Format) of SOP-nn; the Item numbers 1…N on every tab are identical to the S.No. used in that SOP. Do not renumber, insert or delete item columns.
2. Fill only the shaded (cream) header fields and the white table cells. One row = one equipment / unit (tag or ID). Use the drop-down: √ = OK / Pass, X = NOT OK / Fail, NA = Not Applicable / Not Available. Every X must be explained in Remarks.
3. The Frequency / Requirement line under each item is copied from the SOP. Applicable standards and test baselines are printed from SOP Section 3 beneath each table.
4. Totals (√ / X / NA per item) calculate automatically. Sign-off follows SOP Section 6: Checked by (Service Engineer), Verified by (Supervisor / Technical), Witnessed by (Client I/C Fire Services).
5. Make a copy of the required tab(s) per client / site / month; keep this master unaltered. Changes to items require a revision of the corresponding SOP first (item numbers must always match the SOP).
6. Tab 'Example (CL-01)' shows a filled sheet with sample data (blue font) for illustration only. Tab 'Legacy Tab Mapping' maps the September-2020 SRF workbook tabs to this set and lists gaps.

## Legacy Tab Mapping
MAPPING OF LEGACY WORKBOOK TABS (SRF AMC Report – September 2020) TO THE NEW CONTROL COPY
Proposed mapping prepared from tab content – please confirm. 'No SOP' means none of SOP-01 to SOP-26 covers the equipment; no checklist has been created for it.
Legacy tab | State | New checklist | Comment
Hyd-HB CL-01 | Visible | CL-01 + CL-03 | Landing-valve columns → SOP-01; hose-box columns → SOP-03. Legacy 'CL-01' number is superseded by the SOP-based number.
FEH | Visible | CL-01 (+ CL-03) | Hydrant riser (FEH) – same SOP-01 items; hose-box items from SOP-03 where a box is fitted.
F-Monitor CL-02 | Visible | CL-02 | Foam monitors – SOP-02.
W-Monitor | Visible | CL-02 | Water monitors – SOP-02 (covers fixed / portable foam & water monitors).
Air Line CL -03 | Visible | No SOP | Air-line respiratory system – not covered by SOP-01…26. NOTE: legacy 'CL-03' clashes with new CL-03 (Hose Boxes).
SCBA Set | Visible | No SOP | Breathing-apparatus inspection – no SOP.
Sprinkler-WC | Visible | CL-05 | Water-curtain sprinklers – SOP-05 (Water Spray & Drencher).
Sprinkler System | Hidden | CL-05 | Sprinkler / curtain system – SOP-05.
Hose Reel | Visible | CL-09 | First-aid hose reels – SOP-09.
F Trolly | Visible | CL-06 | Foam trolleys – SOP-06.
ABC Fire Ext CL-18 | Visible | CL-11 / CL-26 (partial) | Monthly visual inspection of extinguishers is not an SOP activity. SOP-11 covers hydro-test & pressurisation; SOP-26 covers hanging & mounting. NOTE: legacy 'CL-18' clashes with new CL-18 (Detection & Alarm).
DCP Fire Ext CL-19 | Visible | CL-11 / CL-26 (partial) | As above. NOTE: legacy 'CL-19' clashes with new CL-19 (Inline Foam Inductors).
Co2 Fire Ext | Visible | CL-11 / CL-26 (partial) | As above (portable CO2 extinguishers). Fixed CO2 / clean-agent systems are CL-13.
M-Foam Fire Ext | Visible | CL-11 / CL-22 / CL-26 (partial) | Mechanical-foam / CA foam extinguishers: hydro-test per SOP-11 / SOP-22; mounting per SOP-26.
K -Fire Ext | Visible | CL-11 / CL-26 (partial) | As above.
Wind Socks | Visible | No SOP | Not covered by any SOP.
Air Release valve | Visible | No SOP | Not covered (SOP-15 covers isolation valves of the fire-water network only).
HPT of D Hose | Hidden | No SOP | Hose hydraulic testing – not covered (SOP-03 covers hose boxes, not hose testing).
Diphotehrine Anti HF Kit | Hidden | No SOP | Not covered by any SOP.
Safety Shower CL -1 to CL -4 | Visible | No SOP | Weekly safety-shower / eye-wash checks – not covered by any SOP.
Sheet1 | Visible | — | Empty sheet – dropped.
SOPs with no legacy tab (new checklists, no prior report format): CL-04, 07, 08, 10, 12, 13, 14, 15, 16, 17, 18, 19, 20, 21, 23, 24, 25 – built directly from SOP Section 6.

## CL-01 Hydrant & FB Inlet
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  |  | Reference SOP No. |  |  | Revision |  |  | Effective Date |  |  | Doc. Type / Classification
IFSPL/M&M/CL/001 |  |  | IFSPL/M&M/SOP/001 |  |  | 00 |  |  | 01-10-2026 |  |  | Checklist – Control Copy / Internal
CL-01 ¦ CHECK LIST – FIRE HYDRANTS & FIRE BRIGADE INLET MAINTENANCE
Client Name & Address
PO / Contract No. | [7 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [7 empty] | Date of Service
Frequency | [7 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–10) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/001.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Item 8 | Item 9 | Item 10 | Remarks
|  |  |  | Visual check of coupling washers and blank caps | Lugs assembly, spring and check nut locking operation | Spindle, spindle gasket and handwheel – smooth operation, no bend / damage | Isolation valve – seat, gland, gasket condition and operation | Water tightness (seat) test – 14 Kg/cm² | Hydrostatic (body) test – 21 Kg/cm² | Flow test – 900 LPM (Type A) / 1800 LPM (Type B) at 7 Kg/cm² | Fire Brigade Inlet – NRV, seat washer, spring, gasket, drain valve | Surface scraping, 2 coats primer and 2 coats Fire Red paint; isolation valve black | Hydrant numbering, ON / OFF marking and servicing date label
|  |  |  | Each servicing | Each servicing | Each servicing | Each servicing | As per instruction | As per instruction | As per instruction | Each servicing | Each servicing / as required | Each servicing
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/001, Section 3 (Technical Specifications & Performance Baseline)
• Water Tightness Test (Seat Test): 14 Kg/cm² for both Type A and Type B.
• Hydrostatic Pressure Test (Body Test): 21 Kg/cm² for both Type A and Type B.
• Flow Test Benchmark: Type A requires 900 LPM at 7 Kg/cm²; Type B requires 1800 LPM at 7 Kg/cm².
• Applicable standards: IS 5290 (hydrant landing valve), IS 937 (washers / rubber components), IS 5 Shade 536 (Fire Red paint).
Checked by (Service Engineer) |  |  |  |  | Verified by (Supervisor / Technical) |  |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  |  | Name: |  |  |  |  | Name:
Signature: |  |  |  |  | Signature: |  |  |  |  | Signature:
Date: |  |  |  |  | Date: |  |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-02 Foam-Water Monitors
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  |  | Reference SOP No. |  |  | Revision |  |  | Effective Date |  |  | Doc. Type / Classification
IFSPL/M&M/CL/002 |  |  | IFSPL/M&M/SOP/002 |  |  | 00 |  |  | 01-10-2026 |  |  | Checklist – Control Copy / Internal
CL-02 ¦ CHECK LIST – FIXED & PORTABLE FIRE WATER / FOAM MONITORS MAINTENANCE
Client Name & Address
PO / Contract No. | [7 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [7 empty] | Date of Service
Frequency | [7 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–10) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/002.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Item 8 | Item 9 | Item 10 | Remarks
|  |  |  | Free horizontal and vertical rotation; lock pin, gear and handle condition | Swivel joint / ball bearing – no leakage, smooth rotation | Nozzle – jet, spray and fog pattern, gasket and O-ring | Pick-up tube, strainer and jubilee clips | Isolation valve and drain valve operation | Inlet coupling with NRV (trolley / portable monitors) | Trolley wheels, axle, brake, towing assembly and support leg | Functional / performance test | Painting (2 coats primer + 2 coats Fire Red Shade 536) | Label – date of servicing, date of performance test, ON / OFF position
|  |  |  | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing / as required | Each servicing
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/002, Section 3 (Technical Specifications & Performance Baseline)
• Monitor capacities covered: up to 500 GPM (fixed / portable), 500 – 1000 GPM and 1000 – 2000 GPM (trolley mounted).
• Swivel joint sizes: 2 ½", 3" and 4"; isolation valve sizes: 3" and 4" (fixed / portable) and 4", 6", 8" (trolley mounted).
• Skid mounted monitor: foam monitor 1750 LPM, 4" (100 mm) butterfly valve, 100 mm male / female instantaneous coupling, skid approx. 1200 mm x 800 mm with aluminium chequered plate, approx. 2 m of 100 mm pipe.
• Reference – Foam cum Water Monitor 500 GPM (US): flow 500 GPM at 7 kg/cm²; hydrostatic test pressure 25 kg/cm²; rotation 360°; elevation +75° / -30°; water range 50 m and foam range 45 m at 35°; induction rate 3 %; expansion ratio 1:6; finish Fire Red Shade 536 (IS 5).
• Applicable standards: IS 5 (colours), IS 8442 / UL (swivel joint), API-600 Class 150 (isolation valves).
Checked by (Service Engineer) |  |  |  |  | Verified by (Supervisor / Technical) |  |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  |  | Name: |  |  |  |  | Name:
Signature: |  |  |  |  | Signature: |  |  |  |  | Signature:
Date: |  |  |  |  | Date: |  |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-03 Hose Boxes
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  |  | Reference SOP No. |  |  | Revision |  |  | Effective Date |  |  | Doc. Type / Classification
IFSPL/M&M/CL/003 |  |  | IFSPL/M&M/SOP/003 |  |  | 00 |  |  | 01-10-2026 |  |  | Checklist – Control Copy / Internal
CL-03 ¦ CHECK LIST – DELIVERY HOSE BOXES MAINTENANCE
Client Name & Address
PO / Contract No. | [5 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [5 empty] | Date of Service
Frequency | [5 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–8) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/003.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Item 8 | Remarks
|  |  |  | Front glass panel and key glass – intact | Rubber beading / packing – condition | Hinges and fittings – lubricated and functional | Handle, lock and key availability | Hoses and branch pipe present, clean and correctly stowed | Box mounting and stand – stable and clean | Painting – exterior Fire Red, interior white | Labelling / numbering of hose box
|  |  |  | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing / as required | Each servicing
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/003, Section 3 (Technical Specifications & Performance Baseline)
• Hose box: LDPE construction suitable to accommodate 2 nos. 15 m long fire fighting hoses (Type B) with coupling and branch pipe.
• Finish: exterior Fire Red (IS 5, Shade 536) over 2 coats of primer; interior white; hinged double doors with polycarbonate glazing and locking arrangement.
• Door glass: polycarbonate of proper size with rubber beading.
Checked by (Service Engineer) |  |  |  | Verified by (Supervisor / Technical) |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-04 Foam Pourer-Maker
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  |  | Reference SOP No. |  |  | Revision |  |  | Effective Date |  |  | Doc. Type / Classification
IFSPL/M&M/CL/004 |  |  | IFSPL/M&M/SOP/004 |  |  | 00 |  |  | 01-10-2026 |  |  | Checklist – Control Copy / Internal
CL-04 ¦ CHECK LIST – FOAM POURER / FOAM MAKER SYSTEMS MAINTENANCE
Client Name & Address
PO / Contract No. | [5 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [5 empty] | Date of Service
Frequency | [5 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–8) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/004.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Item 8 | Remarks
|  |  |  | Vapour seal (mica) glass – intact and sealed | Foam pourer line – no leakage | End coupling and blank cap – present, greased, functional | Drain valve – operation | Flange studs and bolts – tight, no corrosion | Foam pourer body – corrosion / damage | Painting of pourer and pipe lines – Fire Red | Tank identification marking on end couplings
|  |  |  | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing / as required | Each servicing
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/004, Section 3 (Technical Specifications & Performance Baseline)
• Foam pourer / maker capacity: 150 to 1000 LPM at 3.5 kg/cm².
• Flange inlet: 50 mm, 65 mm, 80 mm, 100 mm and 150 mm; flange outlet: 80 mm, 100 mm and 150 mm; MS / GI material.
• Vapour seal: mica glass, breakable at a pressure of 1.5 kg/cm².
• End coupling: 63 mm dia male instantaneous coupling (SS / Gun Metal) with provision for NRV fitting.
• Lines supplying foam to one foam pourer are treated as one irrespective of the number or size of lines feeding it.
Checked by (Service Engineer) |  |  |  | Verified by (Supervisor / Technical) |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-05 Spray & Drencher
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  |  | Reference SOP No. |  |  | Revision |  |  | Effective Date |  |  | Doc. Type / Classification
IFSPL/M&M/CL/005 |  |  | IFSPL/M&M/SOP/005 |  |  | 00 |  |  | 01-10-2026 |  |  | Checklist – Control Copy / Internal
CL-05 ¦ CHECK LIST – WATER SPRAY & DRENCHER SYSTEMS MAINTENANCE
Client Name & Address
PO / Contract No. | [5 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [5 empty] | Date of Service
Frequency | [5 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–8) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/005.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Item 8 | Remarks
|  |  |  | Spray nozzles – position, damage, blockage | Nozzle strainers and revolving heads | Pipeline, fittings, hangers and supports | Isolation and drain valves – operation | Pressure gauges and relief valves | System flushing completed | Full flow test – pattern and coverage satisfactory | Valves restored to normal position
|  |  |  | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | After test
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/005, Section 3 (Technical Specifications & Performance Baseline)
• Nozzle: 120° full-cone uniform spray pattern covering approx. 3 m diameter when located approx. 1 m from the shell surface; low impact and minimum rebound.
• Nozzle pressure available on the ring: 1.4 to 6 kgf/cm²; performance data required from 1.5 to 6.0 kgf/cm².
• Nozzle capacities: 1.5 kgf/cm² – 50 / 75 / 100 LPM; 2.0 kgf/cm² – 75 / 100 / 125 LPM; 2.5 kgf/cm² – 75 / 100 / 125 / 150 LPM.
• Non-clogging type; inlet tapered threads per IS 554; MS half coupling 3000 lbs rating per ANSI B 16.11; hexagonal / square outer shape for screwing.
• Material: body copper alloy grade-II (IS 318); deflector brass sheet (IS 410).
Checked by (Service Engineer) |  |  |  | Verified by (Supervisor / Technical) |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-06 Foam Trolleys
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/006 |  | IFSPL/M&M/SOP/006 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-06 ¦ CHECK LIST – FOAM TROLLEY MAINTENANCE
Client Name & Address
PO / Contract No. | [5 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [5 empty] | Date of Service
Frequency | [5 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–7) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/006.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Remarks
|  |  |  | Foam tank – clean, dry, no leakage | Pick-up tube, NRV, strainer and drain valve | Foam inductor – clean and functional (3 % induction) | Couplings and lugs for inductor / branch | Wheels and trolley movement | Foam level / quantity and refilling date marked | Painting – admiralty grey, labelling
|  |  |  | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing / as required
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/006, Section 3 (Technical Specifications & Performance Baseline)
• Foam induction: 3 %.
• Foam inductor: Gun Metal; inlet 63 mm male coupling / 2", 3" or 4" flange; outlet 63 mm female coupling / 2", 3" or 4" flange.
• Drain valve SS 316; pick-up tube PVC 20 mm hose pipe with end fittings; pick-up tube strainer SS 304.
• Foam branch: FB5X / FB10X (as per BIS) – SS / Bronze / Aluminium alloy; foam tank cap (4") PVC as per BS 336.
• Finish: 2 coats of admiralty grey paint (IS 5) over 2 coats of anti-corrosive primer.
Checked by (Service Engineer) |  |  |  | Verified by (Supervisor / Technical) |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-07 Trolley DCP 150Kg
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  |  | Reference SOP No. |  |  | Revision |  |  | Effective Date |  |  | Doc. Type / Classification
IFSPL/M&M/CL/007 |  |  | IFSPL/M&M/SOP/007 |  |  | 00 |  |  | 01-10-2026 |  |  | Checklist – Control Copy / Internal
CL-07 ¦ CHECK LIST – MOBILE TROLLEY MOUNTED DCP SYSTEMS MAINTENANCE (150 KG)
Client Name & Address
PO / Contract No. | [6 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [6 empty] | Date of Service
Frequency | [6 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–9) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/007.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Item 8 | Item 9 | Remarks
|  |  |  | DCP powder condition (no moisture lumps) | Vessel hydrostatic test – 30 kg/cm² for 3 minutes | Valves (incl. LOCK / OPEN marking) and N2 cylinder valves | Hose, nozzle, couplings – no abrasion, cut, choke | Pressure gauge, regulator and safety valve – calibration | Pressure relief vent and filler cap gasket / threads | Pipe lines purged with nitrogen / dry air | Trolley – wheels, brake, towing hook | Painting and labelling – test / refill dates
|  |  |  | Annual | Once in three years | Annual | Annual | Annual | Annual | Annual | Annual | Each servicing
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/007, Section 3 (Technical Specifications & Performance Baseline)
• DCP vessel hydrostatic test: 30 kg/cm² for 3 minutes (or per OEM manual); interval: once in three years.
• Servicing frequency: annual.
• Regulator: Gun Metal, make ESAB, model N-10, max. outlet pressure 10 Bar, max. flow 1000 LPM, service for nitrogen; safety valve vent pressure above 1.5 times (or as per OEM) of delivery working pressure.
• Pressure gauge: Bourdon type, 100 – 150 mm dial, glycerine filled, SS 304 body, sizes 2.5", 3", 4" and 6", with Gun Metal plug-type gauge cocks and copper / SS capillary.
• Finish: Fire Red, IS 5 Shade 536, over epoxy primer.
Checked by (Service Engineer) |  |  |  |  | Verified by (Supervisor / Technical) |  |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  |  | Name: |  |  |  |  | Name:
Signature: |  |  |  |  | Signature: |  |  |  |  | Signature:
Date: |  |  |  |  | Date: |  |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-08 Deluge Valves
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/008 |  | IFSPL/M&M/SOP/008 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-08 ¦ CHECK LIST – FIRE WATER DELUGE VALVES MAINTENANCE
Client Name & Address
PO / Contract No. | [5 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [5 empty] | Date of Service
Frequency | [5 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–7) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/008.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Remarks
|  |  |  | Area cleared of vegetation (100 cm radius) | Bypass and blinds provided before dismantling | Valve internals cleaned; diaphragm, seat, O-ring, gasket checked / replaced | Hydro test at 1.5 times operating pressure | Pilot actuation system – function | Instrumentation tubing – no leakage | Re-installation and functional test
|  |  |  | Before work | Before work | Each servicing | Each servicing | Each servicing | Each servicing | After servicing
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/008, Section 3 (Technical Specifications & Performance Baseline)
• Valve types: globe pattern and butterfly, of various sizes at various locations.
• Hydro test pressure: 1.5 times the operating pressure.
• Cleaning solution: 5 % muriatic acid.
• Spares to be OEM only; spares not covered in the spares list to be supplied with rate reasonability certificate and original invoice.
• Associated parts: pilot valve, solenoid valve, pressure gauge, alarm gong, pressure sensor, drain valve, FSD valves and pulling knobs, diaphragm, actuator (pneumatic / electronic), spindle, seats and washers.
Checked by (Service Engineer) |  |  |  | Verified by (Supervisor / Technical) |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-09 Hose Reels
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/009 |  | IFSPL/M&M/SOP/009 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-09 ¦ CHECK LIST – FIRST AID FIRE HOSE REELS MAINTENANCE
Client Name & Address
PO / Contract No. | [5 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [5 empty] | Date of Service
Frequency | [5 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–7) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/009.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Remarks
|  |  |  | Free rotation / operation of reel | Leakage at joints, swivel and valve | Hose – kinks, cuts, cleaning, French chalk | Shut-off nozzle and ball valve operation | Hydrostatic body test – 21 Kg/cm² | Jet range – 6 m at 7 Kg/cm² | Painting and labelling
|  |  |  | Each servicing | Each servicing | Each servicing | Each servicing | As per instruction | As per instruction | Each servicing / as required
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/009, Section 3 (Technical Specifications & Performance Baseline)
• Hose reel: 30 m long, 20 mm dia, thermoplastic hose as per IS 12585 / hydraulic rubber hose IS 444 Type-2, with 20 mm ball valve.
• Hose: working pressure 10 Kg/cm²; bursting pressure 40 Kg/cm².
• Hydrostatic pressure test (body test): 21 Kg/cm².
• Range (jet length): 6 m at 7 Kg/cm²; flow test: 24 litres per minute at 7 Kg/cm² (as stated in the Scope of Work).
• Drum: swinging 180° wall mounting; hub sides and wall bracket MS sheet (IS 513); swing joint LTB-2 (IS 318); pipe with fittings MS (IS 1239 Part-I); shut-off nozzle ¾" (IS 8090); inlet 20 mm (¾" BSP).
Checked by (Service Engineer) |  |  |  | Verified by (Supervisor / Technical) |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-10 Fire Vehicle Systems
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/010 |  | IFSPL/M&M/SOP/010 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-10 ¦ CHECK LIST – FIRE VEHICLES – ASSOCIATED WATER / FOAM SYSTEMS MAINTENANCE
Client Name & Address
PO / Contract No. | [5 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [5 empty] | Date of Service
Frequency | [5 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–7) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/010.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Remarks
|  |  |  | Hose reel drum rotation and swivel joint | Hose condition (LP / HP / UHP) – cuts, kinks, leakage | Battery operated drum – electrical and manual operation | Monitor rotation, lock, handle and gear | Monitor nozzle pattern – jet / spray / fog | Isolation, ball and butterfly valves; delivery valve | Painting and labelling
|  |  |  | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing / as required
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/010, Section 3 (Technical Specifications & Performance Baseline)
• Low pressure hose reel: 20 mm; length 30 m per the component table (the scope text states 60 m – confirm per vehicle); working pressure 10 Kg/cm², bursting 40 Kg/cm²; hydraulic rubber hose IS 444 Type-2 / thermoplastic hose IS 12585 Type-2; IS 884.
• High pressure hose reel: nylon braided hose 20 mm, 60 m, working pressure 40 Kg/cm², bursting 160 Kg/cm² (UL listed), yellow.
• Ultra high pressure hose reel: nylon braided hose 12.5 / 13 mm, 60 m, working pressure 100 Kg/cm², bursting 400 Kg/cm² (UL listed), yellow.
• Water mist gun: water particle size not more than 250 ± 100 micron; flow up to 145 ± 5 LPM; jet range 20 ± 3 m; spray range 16 ± 3 m; SS 304.
• Delivery valve of centrifugal fire pump per BIS 4928: body / hand wheel LTB-2 (IS 318); spindle brass rod (IS 320).
Checked by (Service Engineer) |  |  |  | Verified by (Supervisor / Technical) |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-11 Extinguisher HPT
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  |  | Reference SOP No. |  |  | Revision |  |  | Effective Date |  |  | Doc. Type / Classification
IFSPL/M&M/CL/011 |  |  | IFSPL/M&M/SOP/011 |  |  | 00 |  |  | 01-10-2026 |  |  | Checklist – Control Copy / Internal
CL-11 ¦ CHECK LIST – HYDRO TESTING & PRESSURISATION OF FIRE EXTINGUISHERS
Client Name & Address
PO / Contract No. | [6 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [6 empty] | Date of Service
Frequency | [6 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–9) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/011.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Item 8 | Item 9 | Remarks
|  |  |  | Calibration certificate of test gauge available | Agent removed; outlets blinded; test with cap / valve | Hydraulic test – 35 Bar for 3 minutes (no leakage / deformation) | Date of hydro test marked on body | Cap assembly, discharge tube, nozzle condition | DCP powder / cartridge / CO2 weight check | Nitrogen pressurisation (if applicable) | Painting, label and tag (not for failed units) | Test certificate issued
|  |  |  | Before start | Each extinguisher | Each extinguisher | Each extinguisher | Each extinguisher | Each extinguisher | As required | Each extinguisher | Each lot
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/011, Section 3 (Technical Specifications & Performance Baseline)
• Hydraulic test pressure: 35 Bar for three minutes (IS 2190).
• Painting: two coats of red oxide primer followed by two coats of red oxide paint, Shade 536 of IS 5.
• Pressurisation: dry nitrogen gas for pressure-type extinguishers.
• A lot of 20 extinguishers shall be refilled within 72 hours of handing over to the Firm's representative.
• Extinguishing agents (dry powder / AFFF) are provided by the Client.
Checked by (Service Engineer) |  |  |  |  | Verified by (Supervisor / Technical) |  |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  |  | Name: |  |  |  |  | Name:
Signature: |  |  |  |  | Signature: |  |  |  |  | Signature:
Date: |  |  |  |  | Date: |  |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-12 MX Foam Generators
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/012 |  | IFSPL/M&M/SOP/012 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-12 ¦ CHECK LIST – MECHANICAL MEDIUM EXPANSION FOAM GENERATORS MAINTENANCE
Client Name & Address
PO / Contract No. | [5 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [5 empty] | Date of Service
Frequency | [5 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–7) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/012.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Remarks
|  |  |  | Foam tank drained, washed; gasket replaced | Level indicator – clean, no leakage | Tank-to-inductor line, inductor and applicator flushed | Pipe connections – no leakage | Water supply isolation valve and NRV | Pressure gauge and re-test of foam generator | Painting
|  |  |  | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | As required
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/012, Section 3 (Technical Specifications & Performance Baseline)
• Foam generator: body / barrel SS 304; nozzle Gun Metal (minimum 4 nos.); mesh and foam screen SS 304; inlet 80 mm SS 304 flange ASA 150.
• Nominal flow 600 LPM; expansion 1:40; foam output 24000 LPM; throw 3.5 m minimum.
• Unit dimension: 600 (L) x 350 (B) x 560 (H) mm ± 10 %; finish with luminous yellow paint.
• Inline inductor: 50 / 80 / 100 mm NB, SS 304 flange ASA 150; induction rate 3 % or variable.
• Level indicator pipe glass ¾" – thickened glass tube (as per sample).
Checked by (Service Engineer) |  |  |  | Verified by (Supervisor / Technical) |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-13 Clean Agent-CO2
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  |  | Reference SOP No. |  |  | Revision |  |  | Effective Date |  |  | Doc. Type / Classification
IFSPL/M&M/CL/013 |  |  | IFSPL/M&M/SOP/013 |  |  | 00 |  |  | 01-10-2026 |  |  | Checklist – Control Copy / Internal
CL-13 ¦ CHECK LIST – CLEAN AGENT / CO2 FIRE SUPPRESSION SYSTEMS MAINTENANCE
Client Name & Address
PO / Contract No. | [7 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [7 empty] | Date of Service
Frequency | [7 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–10) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/013.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Item 8 | Item 9 | Item 10 | Remarks
|  |  |  | Nozzles – position, obstruction, damage | Cylinder pressure recorded; pressure drop < 10 % | Agent weight check; loss < 5 % | Cylinder clamps secure | Hoses – visual examination | Hose pressure test | Actuation test without discharge of agent | Abort switch, alarm, pre-discharge warning | Wightman system | Pipe lines blown through with compressed air
|  |  |  | Each servicing | Each servicing | Each servicing | Each servicing | Annual | Once in five years | Each servicing | Each servicing | Each servicing | Each servicing
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/013, Section 3 (Technical Specifications & Performance Baseline)
• System makes: Siemens, Kidde, etc.; clean agent and CO2.
• Cylinder pressure drop of 10 % of design pressure: replace with charged cylinder (after Fire Officer approval).
• Agent weight loss of 5 %: recommend cylinder for replacement and record to the Client.
• Hose test: 1.5 times maximum container pressure at 130 °F (54.4 °C) or once in five years; annual visual examination.
• Gauge calibration is not required as it could release gas to atmosphere; replacement of cylinders with charge is not provided by the Firm.
Checked by (Service Engineer) |  |  |  |  | Verified by (Supervisor / Technical) |  |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  |  | Name: |  |  |  |  | Name:
Signature: |  |  |  |  | Signature: |  |  |  |  | Signature:
Date: |  |  |  |  | Date: |  |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-14 Tender DCP Systems
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  |  | Reference SOP No. |  |  | Revision |  |  | Effective Date |  |  | Doc. Type / Classification
IFSPL/M&M/CL/014 |  |  | IFSPL/M&M/SOP/014 |  |  | 00 |  |  | 01-10-2026 |  |  | Checklist – Control Copy / Internal
CL-14 ¦ CHECK LIST – DCP SYSTEMS OF FIRE TENDERS MAINTENANCE
Client Name & Address
PO / Contract No. | [6 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [6 empty] | Date of Service
Frequency | [6 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–9) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/014.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Item 8 | Item 9 | Remarks
|  |  |  | Powder decanted and stored in moisture-proof bags | Hydro test – 21 kg/cm² for 30 minutes | Internal painting; gaskets, washers, O-rings replaced | N2 hoses, regulator, gauges and PSV – calibration certificates | Valves, nozzles, hose and hose reel – function | Actuators / cartridges – piercing mechanism | DCP monitor and pneumatic valve operation | Painting, tagging and due dates marked | Hydro test and servicing certificates issued
|  |  |  | Each hydro test | As per due date | Each hydro test | Annual | Annual | Annual | Annual | Each servicing | Each unit
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/014, Section 3 (Technical Specifications & Performance Baseline)
• Hydro test: 21 kg/cm² for 30 minutes; repeat if pressure drops.
• Regulator outlet setting: 14 Kg/cm² ± 0.5 Kg.
• Time schedule: capacity below 500 Kg – 2 weeks; 500 to 800 Kg – 3 weeks; 1000 x 2 Kg – 4 weeks from the date of initiation of work.
• N2 cylinder interconnecting hose: ¼", EN 853, WP 3265 psi, BP 13,060 psi; nitrogen inlet hose: EN 853, ½", WP 4000 psi, BP 16,000 psi.
• Spares as per OEM / OES; replacement of any part is decided by the Client; payment as per actual.
Checked by (Service Engineer) |  |  |  |  | Verified by (Supervisor / Technical) |  |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  |  | Name: |  |  |  |  | Name:
Signature: |  |  |  |  | Signature: |  |  |  |  | Signature:
Date: |  |  |  |  | Date: |  |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-15 Isolation Valves
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/015 |  | IFSPL/M&M/SOP/015 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-15 ¦ CHECK LIST – ISOLATION VALVES OF FIRE WATER NETWORK MAINTENANCE
Client Name & Address
PO / Contract No. | [5 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [5 empty] | Date of Service
Frequency | [5 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–7) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/015.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Remarks
|  |  |  | Valve ID, size and location recorded | Network kept operational during removal (standby valve) | Gland / bush leakage rectified; gland packing | Lubrication; smooth operation through full range | Wheel and operating key | Painting, labelling and ON / OFF marking | Performance test witnessed
|  |  |  | Each valve | During work | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/015, Section 3 (Technical Specifications & Performance Baseline)
• Valve sizes covered: 1.5", 2", 3", 4", 6", 8", 10", 12", 14", 16", 18" and 20".
• Replacement valves: up to 4", Class 150, as per API-600; makes Norflow / Audco / Kirloskar / L&T.
• Wheels: cast iron for valves ranging from 1.5" to 16".
• Painting: 2 coats; labelling and marking as per applicable standards and colour code.
Checked by (Service Engineer) |  |  |  | Verified by (Supervisor / Technical) |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-16 FW Tank Cleaning
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/016 |  | IFSPL/M&M/SOP/016 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-16 ¦ CHECK LIST – CLEANING OF FIRE WATER TANKS AT FIRE STATIONS
Client Name & Address
PO / Contract No. | [5 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [5 empty] | Date of Service
Frequency | [5 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–6) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/016.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Remarks
|  |  |  | Work permit and intimation to Fire Services | Water drained completely | Safety measures for depth > 1.8 m | Sludge and accumulated material removed | Sludge disposed of outside premises | Tiles, flooring and walls – no damage
|  |  |  | Before work | Each cleaning | Each cleaning | Each cleaning | Each cleaning | Each cleaning
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/016, Section 3 (Technical Specifications & Performance Baseline)
• Tank capacity: up to 250 m³; RCC construction, below ground level with open top at ground level.
• Draining: using the pump available at the fire station.
• Depth more than 1.8 m: necessary personnel safety measures are mandatory.
• Sludge disposal: at an appropriate place outside the Client's premises.
Checked by (Service Engineer) |  |  |  | Verified by (Supervisor / Technical) |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-17 Buckets & Stands
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/017 |  | IFSPL/M&M/SOP/017 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-17 ¦ CHECK LIST – FIRE BUCKETS & BUCKET STANDS MAINTENANCE
Client Name & Address
PO / Contract No. |  |  |  |  | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. |  |  |  |  | Date of Service
Frequency |  |  |  |  | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–5) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/017.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Remarks
|  |  |  | Buckets – rust removed, cleaned | Bucket painting – external Fire Red, internal white | Sand / water refilled after paint dry | Bucket stand – cleaned, stable | Bucket stand painting
|  |  |  | Each servicing | As required | Each servicing | Each servicing | As required
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/017, Section 3 (Technical Specifications & Performance Baseline)
• Bucket: external Fire Red, internal white; one coat of primer before painting.
• Bucket stand: one coat of primer and one coat of Fire Red paint where required.
• Bucket content: sand or water, replaced after paint has dried.
Checked by (Service Engineer) |  |  | Verified by (Supervisor / Technical) |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-18 Detection & Alarm
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/018 |  | IFSPL/M&M/SOP/018 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-18 ¦ CHECK LIST – FIRE DETECTION & ALARM SYSTEMS MAINTENANCE
Client Name & Address
PO / Contract No. | [5 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [5 empty] | Date of Service
Frequency | [5 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–7) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/018.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Remarks
|  |  |  | Panel – power supply, indications and faults | Optical smoke detectors – cleaned and tested | Beam detector – alignment and test | Manual call points – operation test | Hooter – operation | Zone indication on panel for each test | System restored to normal
|  |  |  | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | Each servicing | After test
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/018, Section 3 (Technical Specifications & Performance Baseline)
• System type: conventional fire detection and alarm system.
• Components: optical smoke detector, beam detector, manual call point, panel and hooter.
• Spares and consumables required for repair and servicing are in the Firm's scope; quantity as per the price format.
• Scaffolding / ladder for access to detectors at height is provided by the Firm.
Checked by (Service Engineer) |  |  |  | Verified by (Supervisor / Technical) |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-19 Inline Inductors
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/019 |  | IFSPL/M&M/SOP/019 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-19 ¦ CHECK LIST – INLINE FOAM INDUCTORS MAINTENANCE
Client Name & Address
PO / Contract No. |  |  |  | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. |  |  |  | Date of Service
Frequency |  |  |  | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–4) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/019.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Remarks
|  |  |  | Pick-up tube / pipeline – washed, no leakage | Inductor dismantled (where part of nurser) and cleaned | 3 % induction test with AFFF | Painting – Fire Red
|  |  |  | Each servicing | Each servicing | Annual | As required
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/019, Section 3 (Technical Specifications & Performance Baseline)
• Induction rate: 3 % (test with AFFF).
• Full system test: at least once in a year.
• Inductor material: Gun Metal; foam pick-up tube hard PVC 20 mm with SS 304 strainer (where applicable).
• Finish: Fire Red, Shade 536 (IS 5), surface tolerant epoxy primer before finish painting.
Checked by (Service Engineer) |  |  | Verified by (Supervisor / Technical) |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-20 Vehicle Tank Cleaning
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/020 |  | IFSPL/M&M/SOP/020 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-20 ¦ CHECK LIST – CLEANING OF FOAM & WATER TANKS OF FIRE VEHICLES
Client Name & Address
PO / Contract No. | [5 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [5 empty] | Date of Service
Frequency | [5 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–7) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/020.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Remarks
|  |  |  | Foam / water drained and stored as per procedure | Sludge removed and disposed of properly | Tanks washed with water | Level indicator and pipelines – clean, no leakage | Isolation valve, NRV – cleaned / oiled | Corrosion spots – anti-corrosion paint | Baffle plates – integrity, nuts and bolts
|  |  |  | Each cleaning | Each cleaning | Each cleaning | Each cleaning | Each cleaning | Each cleaning | Each cleaning
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/020, Section 3 (Technical Specifications & Performance Baseline)
• Foam tank capacities: 50, 150, 500, 800, 1000, 3000 and 8000 litres.
• Water tank capacities: 500, 1500, 2000, 5000, 7000 and 12000 litres.
• Material of tanks: SS-316; baffle plate nuts and bolts SS-316.
• Accessories (oil, cloth, rubbing items, nuts and bolts for baffle plates) are provided by the Firm.
Checked by (Service Engineer) |  |  |  | Verified by (Supervisor / Technical) |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-21 OH Foam Tank Cleaning
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/021 |  | IFSPL/M&M/SOP/021 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-21 ¦ CHECK LIST – CLEANING OF OVERHEAD FOAM STORAGE TANKS
Client Name & Address
PO / Contract No. | [5 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [5 empty] | Date of Service
Frequency | [5 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–6) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/021.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Remarks
|  |  |  | Foam concentrate drained into drums | Sludge removed and disposed of properly | Tank washed with water | Filling pipeline / hose – clean, no leakage | Isolation valve and NRV – cleaned / oiled | Tank condition – no damage
|  |  |  | Each cleaning | Each cleaning | Each cleaning | Each cleaning | Each cleaning | After cleaning
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/021, Section 3 (Technical Specifications & Performance Baseline)
• Overhead foam storage tank capacity: 5000 litres; PVC; installed on a metal structure.
• Foam concentrate: AFFF; drums provided by the Client.
• Accessories (oil, cloth, rubbing items) provided by the Firm.
Checked by (Service Engineer) |  |  |  | Verified by (Supervisor / Technical) |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-22 CA Foam-Mist Ext
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/022 |  | IFSPL/M&M/SOP/022 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-22 ¦ CHECK LIST – SERVICING & HYDRO TESTING OF CA FOAM / WATER MIST EXTINGUISHERS
Client Name & Address
PO / Contract No. | [5 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [5 empty] | Date of Service
Frequency | [5 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–7) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/022.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Remarks
|  |  |  | Calibration certificate of test gauge available | Hydraulic pressure test (not below 35 Bar) | PSV setting | Cap assembly, discharge hose, gun | Air cylinder pressure | Painting, labelling and tagging | Test certificate issued
|  |  |  | Before start | Each extinguisher | Each extinguisher | Each extinguisher | Each extinguisher | Each extinguisher | Each extinguisher
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/022, Section 3 (Technical Specifications & Performance Baseline)
• Hydraulic test pressure: as per OEM recommendation but not below 35 Bar.
• Painting: two coats of yellow primer followed by two coats of red paint, Shade 536 of IS 5.
• All material, equipment, paint, brushes, primer and labelling stickers are arranged by the Firm.
• Safety guard / cage shall be used during hydraulic pressure testing.
Checked by (Service Engineer) |  |  |  | Verified by (Supervisor / Technical) |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-23 Air Compressors
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/023 |  | IFSPL/M&M/SOP/023 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-23 ¦ CHECK LIST – SERVICING & HYDRO TESTING OF AIR COMPRESSORS (TYRE AIR FILLING)
Client Name & Address
PO / Contract No. | [5 empty] | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. | [5 empty] | Date of Service
Frequency | [5 empty] | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–7) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/023.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Remarks
|  |  |  | Air filter replaced | Pressure gauge replaced | Lubricating oil changed | Pressure switch calibrated (NABL) | Air vessel hydro test – 15 Kg/cm² for 15 minutes | Test date and due date marked on tank | Test certificate issued
|  |  |  | Each servicing | Each servicing | Each servicing | Each servicing | As per due date | Each test | Each air vessel
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/023, Section 3 (Technical Specifications & Performance Baseline)
• Air vessel hydraulic test: 15 Kg/cm² for 15 minutes; no drop in pressure.
• Pressure switch calibration by an NABL approved firm.
• Work completion: within 5 days from the date of start of work for each compressor.
• Compressors covered (indicative): TOYO DTY 2 and K G Khosla AB 7.75 at the fire stations.
Checked by (Service Engineer) |  |  |  | Verified by (Supervisor / Technical) |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-24 Weighing M-c Calib
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/024 |  | IFSPL/M&M/SOP/024 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-24 ¦ CHECK LIST – CALIBRATION OF WEIGHING MACHINES
Client Name & Address
PO / Contract No. |  |  |  |  | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. |  |  |  |  | Date of Service
Frequency |  |  |  |  | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–5) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/024.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Remarks
|  |  |  | Machine make, capacity and serial number recorded | Calibration by NABL approved firm | Completed within 5 days from receipt | Calibration certificate obtained | Machine returned to Client with certificate
|  |  |  | Each calibration | Each calibration | Each calibration | Each machine | Each machine
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/024, Section 3 (Technical Specifications & Performance Baseline)
• Calibration agency: NABL approved firm.
• Time: within 5 days from the date of receipt of the machine.
• Machines in present status: OMEGA 50 / 200 / 500 Kg; V K Makwana & Company 200 Kg (3 nos.).
• A calibration certificate from the approved laboratory is required for each machine.
Checked by (Service Engineer) |  |  | Verified by (Supervisor / Technical) |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-25 Digital Level Calib
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/025 |  | IFSPL/M&M/SOP/025 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-25 ¦ CHECK LIST – SERVICING & CALIBRATION OF DIGITAL LEVEL INDICATORS (OVERHEAD FOAM TANK)
Client Name & Address
PO / Contract No. |  |  |  | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. |  |  |  | Date of Service
Frequency |  |  |  | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–4) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/025.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Remarks
|  |  |  | Activity planned with annual foam tank cleaning | Probe and display – servicing and connection check | Calibration per OEM guidelines (NABL approved firm) | Calibration certificate issued
|  |  |  | Each cycle | Each cycle | Each cycle | Each indicator
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/025, Section 3 (Technical Specifications & Performance Baseline)
• Instrument: capacitance continuous level indicator; Model MPILC; make SAPCON Instruments Pvt. Ltd.
• Calibration: as per OEM guidelines, at Central Fire Station, Gandhar, by an NABL approved firm.
• Work clubbed with annual cleaning of the overhead foam tank.
Checked by (Service Engineer) |  |  | Verified by (Supervisor / Technical) |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## CL-26 Ext Hanging-Mounting
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  | Reference SOP No. |  | Revision |  | Effective Date |  | Doc. Type / Classification
IFSPL/M&M/CL/026 |  | IFSPL/M&M/SOP/026 |  | 00 |  | 01-10-2026 |  | Checklist – Control Copy / Internal
CL-26 ¦ CHECK LIST – HANGING & MOUNTING OF PORTABLE FIRE EXTINGUISHERS
Client Name & Address
PO / Contract No. |  |  |  | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. |  |  |  | Date of Service
Frequency |  |  |  | Month / Period
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–4) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/026.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Remarks
|  |  |  | Location approved by Mines Fire Officer | Bracket / hanger fixed with suitable filling material | Strength test by hanging the extinguisher | Extinguisher box mounted (where applicable)
|  |  |  | Each installation | Each installation | Each installation | Each installation
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 0
Total √ (OK / Pass) |  |  |  | 0 | 0 | 0 | 0
Total X (NOT OK / Fail) |  |  |  | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/026, Section 3 (Technical Specifications & Performance Baseline)
• Extinguishers: portable fire extinguishers as defined in IS 15683.
• Mounting: wall mounting bracket and screws provided by the Firm at no extra cost; tools arranged by the Firm.
• Fixing: screwed with suitable filling material for strength and stability.
• Frequency: as and when required.
Checked by (Service Engineer) |  |  | Verified by (Supervisor / Technical) |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________

## Example (CL-01)
INDUS FIRE SAFETY PRIVATE LIMITED
Corporate Office: 903, Atlantis Heights, Sarabhai Compound, Vadodara-390 023, India. Tele: 0265 2343441, 2343442, 2341633 ¦ Email: maint.ifss@yahoo.com ¦ Web: www.indusfiresafety.com
Checklist Doc. No. |  |  | Reference SOP No. |  |  | Revision |  |  | Effective Date |  |  | Doc. Type / Classification
IFSPL/M&M/CL/001 |  |  | IFSPL/M&M/SOP/001 |  |  | 00 |  |  | 01-10-2026 |  |  | Checklist – Control Copy / Internal
ILLUSTRATIVE EXAMPLE – SAMPLE DATA ONLY (NOT A REAL RECORD) ¦ CL-01 ¦ CHECK LIST – FIRE HYDRANTS & FIRE BRIGADE INLET MAINTENANCE
Client Name & Address |  |  | SAMPLE CLIENT LTD., Plot 00, Industrial Estate, Vadodara
PO / Contract No. |  |  | PO-0000 (sample) |  |  |  |  | Job |  | AMC – Testing, inspection & maintenance of fire protection equipment
Work Order / Ref. No. |  |  | WO-0000 (sample) |  |  |  |  | Date of Service |  | 01-10-2026
Frequency |  |  | Monthly |  |  |  |  | Month / Period |  | October – 2026
Note: Put '√' for OK / Pass, 'X' for NOT OK / Fail and 'NA' for Not Applicable / Not Available. Record every abnormality in the Remarks column. Item numbers (1–10) are identical to the numbering in Section 6 (Check List Format) of IFSPL/M&M/SOP/001.
SN | Area / Plant | ID No. | Location | Item 1 | Item 2 | Item 3 | Item 4 | Item 5 | Item 6 | Item 7 | Item 8 | Item 9 | Item 10 | Remarks
|  |  |  | Visual check of coupling washers and blank caps | Lugs assembly, spring and check nut locking operation | Spindle, spindle gasket and handwheel – smooth operation, no bend / damage | Isolation valve – seat, gland, gasket condition and operation | Water tightness (seat) test – 14 Kg/cm² | Hydrostatic (body) test – 21 Kg/cm² | Flow test – 900 LPM (Type A) / 1800 LPM (Type B) at 7 Kg/cm² | Fire Brigade Inlet – NRV, seat washer, spring, gasket, drain valve | Surface scraping, 2 coats primer and 2 coats Fire Red paint; isolation valve black | Hydrant numbering, ON / OFF marking and servicing date label
|  |  |  | Each servicing | Each servicing | Each servicing | Each servicing | As per instruction | As per instruction | As per instruction | Each servicing | Each servicing / as required | Each servicing
1 | P-01 | SAMPLE/HYD/01 | Near pump house | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | P-01 | SAMPLE/HYD/02 | North side tank farm | √ | √ | √ | √ | √ | √ | √ | √ | √ | NA
3 | P-02 | SAMPLE/HYD/03 | Main gate road | √ | X | √ | √ | √ | √ | √ | √ | √ | √ | Item 2 failed: spring weak – replaced; re-test OK (sample remark)
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Equipment / units checked (nos.) |  |  |  | 3
Total √ (OK / Pass) |  |  |  | 3 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2
Total X (NOT OK / Fail) |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total NA |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Remarks / Observations (including corrective actions, spares replaced and pending points)
Applicable standards & performance baseline – IFSPL/M&M/SOP/001, Section 3 (Technical Specifications & Performance Baseline)
• Water Tightness Test (Seat Test): 14 Kg/cm² for both Type A and Type B.
• Hydrostatic Pressure Test (Body Test): 21 Kg/cm² for both Type A and Type B.
• Flow Test Benchmark: Type A requires 900 LPM at 7 Kg/cm²; Type B requires 1800 LPM at 7 Kg/cm².
• Applicable standards: IS 5290 (hydrant landing valve), IS 937 (washers / rubber components), IS 5 Shade 536 (Fire Red paint).
Checked by (Service Engineer) |  |  |  |  | Verified by (Supervisor / Technical) |  |  |  |  | Witnessed by (Client I/C Fire Services)
Name: |  |  |  |  | Name: |  |  |  |  | Name:
Signature: |  |  |  |  | Signature: |  |  |  |  | Signature:
Date: |  |  |  |  | Date: |  |  |  |  | Date:
For Indus Fire Safety Private Limited – Authorised Signatory (Seal & Signature): ______________________________